## Slide 1
Block Diagrams

## Slide 2
Thermal Controller
To Cryogenic
Control Valve
From Temp
Sensor
Max485
Module
Microcontroller
AC 230V
Relay Module
RTC
SD
Module
+5V
+5V
AC-DC
Converter
+24V
NC
+24V
+12V
+12V
Modbus

## Slide 3
Microcontroller
(Arduino Uno)
AC 230V
+5V
AC-DC
Converter
+24V
DC-DC
Converter
+12V
DC-DC
Converter
Max485
Module
DE
RE
RO
DI
8
8
9
10
RTC
DAT
RST
CLK
5
7
2
LCD
SDA
SCL
A5
A4
RELAY
IN2
IN1
3
4
A2
A3
Manual
Mode
ON/OFF
+5V
GND
A
B
+5V
GND
+5V
GND
+5V
GND
+5V
+5V
SD
Module
+12V
GND
+12V
RK330-2
Sensor
GND
COM
NO
+24V
GND
Solenoid
Valve
Modbus
Box 1

## Slide 4
Microcontroller
(Arduino Uno)
AC 230V
+5V
AC-DC
Converter
+24V
DC-DC
Converter
+12V
DC-DC
Converter
DHT22
Module
DHTPIN
8
RTC
DAT
RST
CLK
5
7
2
LCD
SDA
SCL
A5
A4
RELAY
IN2
IN1
3
4
A2
A3
Manual
Mode
ON/OFF
+
-
+5V
GND
+5V
GND
+5V
GND
+5V
+5V
SD
Module
+12V
GND
COM
NO
+24V
GND
Solenoid
Valve
+5V
GND
Box 1 (change sensor)

## Slide 5
Microcontroller
(Arduino Uno)
AC 230V
+5V
AC-DC
Converter
+24V
DC-DC
Converter
+12V
DC-DC
Converter
Max31855
Module
CS
9
8
10
RTC
DAT
RST
CLK
5
7
2
LCD
SDA
SCL
A5
A4
RELAY
IN2
IN1
A0
A1
A2
A3
Manual
Mode
ON/OFF
+
-
+5V
GND
+5V
GND
+5V
GND
+5V
+5V
SD
Module
+12V
GND
COM
NO
+24V
GND
Solenoid
Valve
+5V
GND
DO
CLK
Box 1 (change sensor)

## Slide 6
Microcontroller
(Arduino Uno)
AC 230V
+5V
AC-DC
Converter
+24V
DC-DC
Converter
+12V
DC-DC
Converter
Max31865
Module
CS
9
8
10
RTC
DAT
RST
CLK
5
7
2
LCD
SDA
SCL
A5
A4
RELAY
IN2
IN1
3
4
A2
A3
Manual
Mode
ON/OFF
+
-
+5V
GND
+5V
GND
+5V
GND
+5V
+5V
SD
Module
+12V
GND
COM
NO
+24V
GND
Solenoid
Valve
+5V
GND
DO
DI
12
CLK
PT100
Box 1 (change sensor, PT100)

## Slide 7
Microcontroller
(Arduino Mega)
AC 230V
+5V
AC-DC
Converter
+24V
DC-DC
Converter
+9V
DC-DC
Converter
Max31865
Module
CS
11
9
10
RTC
DAT
RST
CLK
2
3
4
LED
Y
R
34
35
RELAY
IN2
IN1
22
29
28
Manual
Mode
ON/OFF
+
-
+5V
GND
GND
+5V
GND
+5V
+5V
SD
+9V
GND
COM
NO
+24V
GND
Solenoid
Valve
+5V
GND
DO
DI
8
CLK
SS
MOSI
SCK
MISO
52
51
53
50
G
36
PT100
LED
Module
+5V
GND
SDA
SCL
SDA
SCL
20
21
Box 2 (Mega)

## Slide 8
Microcontroller
(Arduino Uno)
+5V
+24V
DC-DC
Converter
+12V
DC-DC
Converter
Max31865
Module
CS
9
8
10
+
-
+12V
GND
+5V
GND
DO
DI
12
CLK
PT100
Distributed Controller
Max485
Module
DE
RE
RO
DI
8
8
9
10
+5V
GND
A
B
+12V
RK330-2
Sensor
GND
Modbus
Max485
Module
DE
RE
RO
DI
8
8
9
10
+5V
GND
A
B
+24V
Arduino
Mega
GND
Modbus
RELAY
IN1
22
+5V
GND
COM
NO
+24V
GND
Solenoid
Valve
+
Notes: Need to update pin numbers and arrow directions.

## Slide 9
Program Flowchart

## Slide 10
Setup:
Serial Terminal, Initialize variables, Display LEDs, RTC
Max31865, Relay, Mode and ONOFF Switches, microSD
Get time from RTC
Get temperature from Max31865
Display temperature on LEDs & Serial Terminal
Manual Mode?
Read states of MODE and ONOFF switches
Turn on/off Relay and light corresponding LED according to ONOFF switch
*
Y
N
Cont on
next pg
To*

## Slide 11
Cooling?
Turn on Relay and corresponding LED
Temp < Lower Limit?
Turn off Relay and corresponding LED. Set cooling = false
Turn off Relay and corresponding LED
Temp < Upper Limit?
Turn off Relay and corresponding LED. Set cooling = true
To*
Y
Y
Y
N
N
N
N
From
prev pg